## R4
Proposal #: DF/021375/2018/R4 | [16 empty] | 05.01.2019
Item No. |  |  | (1) | (32), (33) | (2), (26) | 29,30 | 3, 4, 34,35 | (13),(14), (22),(28) (31) | (5), (6) | (18),(19), (20),(21), (27) | (7),(8),(10) | (9) | 36 | (11), (12) | (15),(16),(17) | (24), (25) | (23)
Application |  |  | Fan BF-1 (3520 cmh, 350 mmwg, 120 deg C) | Fan BF-32,33 (22000 cmh, 350 mmwg, 90 deg C) | Fan BF-2, 26 (22000 cmh, 350 mmwg, 120 deg C) | Fan BF-3,4,29,30 (16500 cmh, 350 mmwg) | Fan BF-34,35(16500 cmh, 350 mmwg, 120 deg C) | Fan BF-13,14,22,28,31 (11000 cmh, 350 mmwg, 50 deg C) | Fan BF-5,6 (11000 cmh, 350 mmwg, 120 deg C) | Fan BF-18,19,20,21,27 (5500 cmh, 350 mmwg, 50 deg C) | Fan BF-7,8,10 (5500 cmh, 350 mmwg, 120 deg C) | Fan BF-9 (13750 cmh, 350 mmwg, 120 deg C) | Fan BF-36 (13750 cmh, 350 mmwg, 90 deg C) | Fan BF-11,12 (2310 cmh, 350 mmwg, 80 deg C) | Fan BF-15,16,17 (8800 cmh, 350 mmwg, 50 deg C) | Fan BF-24,25 (8800 cmh, 350 mmwg, 120 deg C) | Fan BF-23 (27500 cmh, 350 mmwg, 120 deg C)
Reitz Fan Model No. |  |  | KXE 050-005930-221 (SISW) | KXE 045-040015-221 (SISW) | KXE 050-040015-221 (SISW) | KXE 040-028015-221 (SISW) | KXE 050-028015-251 (SISW) | KXE 040-020015-251 (SISW) | KXE 050-020015-261 (SISW) | KXE 040-009215-281 (SISW) | KXE 050-009215-291 (SISW) | KXE 050-025015-261 (SISW) | KXE 045-025015-231 (SISW) | KXE 045-004230-00 (SISW) | KXE 040-016015-261 (SISW) | KXE 050-016015-281 (SISW) | KXE 050-050015-221 (SISW)
Quantity |  |  | 1 No. | 2 Nos. | 2 Nos. | 2 Nos. | 4 Nos. | 5 Nos. | 2 Nos. | 5 Nos. | 3 Nos. | 1 No. | 1 No. | 2 Nos. | 3 Nos. | 2 Nos. | 1 No.
Arrangement |  |  | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling | Impeller overhung coupled to motor through flexible coupling
Impeller Type |  |  | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed | Backward curved bladed
DUTY PARAMETERS
Capacity |  | M3/Hr | 3520 | 22000 | 22000 | 16500 | 16500 | 11000 | 11000 | 5500 | 5500 | 13750 | 13750 | 2310 | 8800 | 8800 | 27500
Static Pressure |  | mm WG | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Total Pressure |  | mm WG | 352 | 354 | 353 | 354 | 353 | 353 | 352 | 352 | 352 | 352 | 354 | 375 | 352 | 352 | 353
Temperature |  | Deg.C | 120 | 90 | 120 | 50 | 120 | 50 | 120 | 50 | 120 | 120 | 90 | 80 | 50 | 120 | 120
Density |  | Kg/M3 | 0.864 | 1.0556 | 0.8632 | 1.0503 | 0.8632 | 1.0503 | 0.8632 | 1.0503 | 0.8632 | 0.8632 | 0.934 | 0.962 | 1.0503 | 0.8632 | 0.8632
Fan speed |  | RPM | 2900 | 1470 | 1461 | 1463 | 1459 | 1460 | 1466 | 1439 | 1452 | 1445 | 1460 | 2900 | 1435 | 1454 | 1456
Fan shaft power |  | KW | 4.66 | 25.18 | 25.5 | 18.86 | 18.47 | 12.2 | 12.36 | 6.7 | 7.25 | 15.39 | 16.8 | 3.5 | 10.11 | 10.35 | 32.2
Static efficiency |  | % | 71.9983 | 83.2784 | 82.2333 | 83.3888 | 85.1496 | 85.9406 | 84.8281 | 78.2444 | 72.3086 | 85.1588 | 78.0115 | 62.9085 | 82.9654 | 81.0415 | 81.4033
Total efficiency |  | % | 72.4097 | 84.2301 | 82.9382 | 84.3418 | 85.8794 | 86.6772 | 85.3128 | 78.6915 | 72.7218 | 85.6454 | 78.9031 | 67.402 | 83.4395 | 81.5046 | 82.1011
Minimum recommended capacity of motor |  |  | 7.5 kW / 2 pole -Customer Scope | 30 kW / 4 pole -Customer Scope | 30 kW / 4 pole -Customer Scope | 30 kW / 4 pole -Customer Scope | 30 kW / 4 pole -Customer Scope | 18.5 kW / 4 pole -Customer Scope | 18.5 kW / 4 pole -Customer Scope | 15 kW / 4 pole -Customer Scope | 18.5 kW / 4 pole -Customer Scope | 18.5 kW / 4 pole -Customer Scope | 22 kW / 4 pole -Customer Scope | 5.5 kW / 2 pole / 132S-Customer Scope | 15 kW / 4 pole -Customer Scope | 22 kW / 4 pole -Customer Scope | 45 kW / 4 pole -Customer Scope
GD2 of fan rotating parts |  | Kg.M2 | 3 | 93 | 95 | 65 | 75 | 47 | 57 | 47 | 55 | 61 | 58 | 2.25 | 40 | 71 | 102
Full load torque |  | Kg-m | 1.5429 | 16.4474 | 16.759 | 12.3781 | 12.1554 | 8.0235 | 8.0955 | 4.4707 | 4.7943 | 10.2265 | 10.5 | 1.1589 | 6.7648 | 6.8349 | 21.235
Starting torque |  | Kg-m | 0.22372 | 2.3849 | 2.4301 | 1.7948 | 1.7625 | 1.1634 | 1.1738 | 0.64825 | 0.69518 | 1.4828 | 1.52 | 0.16803 | 0.9809 | 0.99106 | 3.0791
CONSTRUCTIONAL FEATURES:
1 | IMPELLER
| Diameter | mm | 562 | 1105 | 1148 | 1047 | 1122 | 1000 | 1047 | 1012 | 1047 | 1059 | 1008 | 512 | 955 | 1122 | 1162
Centre / Back plate
| Material |  | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2
| Thickness (6 thk. min- Cust.Req) | mm | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 ( 6thk. Not required) | 6 | 6 | 6
| Liners, if any, |  | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided
Shroud
| Material |  | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2
| Thickness (4 thk. min- Cust.Req) | mm | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 ( 4thk. Not required) | 5 | 5 | 5
Blade
| Material |  | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2
| Thickness (4 thk. min- Cust.Req) | mm | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 ( 4thk. Not required) | 5 | 5 | 5
| Liners, if any, |  | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided | 3 thk criss cross (CrC) liners provided
| Tip speed | m/sec | 85.2929 | 85.0076 | 87.7749 | 80.1622 | 85.6696 | 76.4067 | 80.3265 | 76.2114 | 79.5594 | 80.0833 | 80 | 77.7045 | 71.7189 | 85.376 | 88.5413
| Weight of impeller (approx.) | kgs | 20 | 140 | 137 | 113 | 118 | 94 | 104 | 94 | 104 | 107 | 102 | 20 | 87 | 117 | 139
2 | SHAFT
| Material |  | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8) | 080 M40 (EN8)
| Diameter at hub | mm | 35 | 55 | 55 | 55 | 55 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 50 | 50 | 65
| Diameter at bearing | mm | 45 | 65 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 60 | 60 | 45 | 60 | 60 | 75
| Critical speed | RPM | 4500 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 4500 | 2250 | 2250 | 2250
| Weight of shaft (approx.) | kgs | 15 | 36 | 36 | 36 | 36 | 30 | 30 | 29 | 29 | 29 | 29 | 15 | 29 | 29 | 52
Shaft seal
| Type |  | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings | Gland type with packings
| Material |  | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2
3 | INLET CONE
| Material |  | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:2062 / S235J2
| Thickness | mm | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 5
4 | CASING / INLET BOX
| Material |  | IS:1079 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:1079 / S235J2 | IS:2062 / S235J2
| Thickness (4 thk. min) | mm | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5
| Liner, if any |  | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided | Not provided
5 | INLET DAMPER
| Type |  | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper (manual) operated | Inlet Butterfly Damper (manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper (manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet Butterfly Damper(manual) operated | Inlet butterfly damper with actuator (On-Off type only)
| Size | mm | 400 | 630 | 630 | 560 | 560 | 500 | 500 | 400 | 400 | 560 | 500 | 224 | 500 | 500 | 710
6 | PEDESTAL |  | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals | Full height pedestals
| Material |  | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2 | IS:2062 / S235J2
| Weight (approx.) | kgs | 100 | 250 | 250 | 150 | 150 | 150 | 150 | 100 | 100 | 160 | 160 | Later | 100 | 100 | 350
7 | BEARING
| Size |  | 22210 EK | 22215 EK | 22215 EK | 22215 EK | 22215 EK | 22213 EK | 22213 EK | 22213 EK | 22213 EK | 22213 EK | 22213 EK | 22210 EK | 22213 EK | 22213 EK | 22217 EK
| Make |  | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN | SKF / FAG /NBC / Timken / NTN
8 | BEARING HOUSING
| Size |  | SN 510 | SN 515 | SN 515 | SN 515 | SN 515 | SN 513 | SN 513 | SN 513 | SN 513 | SN 513 | SN 513 | SN 510 | SN 513 | SN 513 | SN 517
| Lubrication |  | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease | Grease
| Make |  | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco | SKF/Masta/Arun/Winco/Sibco
9 | COUPLING
| Size |  | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2 | Resilient type with minimum SF 2
| Make |  | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon | Flexocon / Wellman / GBM / Fenner / Elecon
10 | Approx. weight of fan | Kgs. | 300 | 900 | 920 | 650 | 700 | 600 | 600 | 450 | 500 | 670 | 900 | 160 | 490 | 590 | 1250